## Sheet1
Power Battery calculation and comparisonsheet
Requirements
Fill out the field marked in yellow to see the specifications of your batterypack below |  | input | unit | range | Info
|  | 110 | V nom | 12 - 800 | The nominal voltage the application requires
|  | 48 | kW | < 1000 | The maximum power needed
|  | 50 | kWh | <500 | The amount of energy required
calc (not visible)
|  | 436.3636 | A |  | peak current needed
|  | 454.5455 | Ah |  | Amount of capacity needed
module specifications (data: not visible)
|  | extreme | endurance | extreme | endurance
|  | 21700-12P | 21700-12P | 21700-8P | 21700-8P | LiFePo4 50Ah | LiFePo4 110Ah | LiFePo4 400Ah | LiFePo4 1000Ah
| minimum voltage (V) | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
| Nominal voltage (V) | 3.6 | 3.6 | 3.6 | 3.6 | 3.2 | 3.2 | 3.2 | 3.2
| Maximum voltage (V) | 4.2 | 4.2 | 4.2 | 4.2 | 3.6 | 3.6 | 3.6 | 3.6
| capacity (Ah) | 50.4 | 58.8 | 33.6 | 39.2 | 50 | 110 | 400 | 1000
| Energy (kWh) | 0.18144 | 0.21168 | 0.12096 | 0.14112 | 0.16 | 0.352 | 1.28 | 3.2
| volume (L) | 0.54 | 0.54 | 0.38 | 0.38 | 0.77 | 1.44 | 8.86 | 22.4
| weight (Kg) | 0.988 | 0.976 | 0.727 | 0.719 | 1.37 | 2.79 | 13.5 | 41
| Continuous discharge current (A) | 300 | 115 | 200 | 75 | 100 | 110 | 1200 | 3000
| Maximum discharge current 50%duty cycle (A) | 420 | 175 | 280 | 115 | 270 | 275 | 1600 | 4000
| Peak discharge current(A) | 540 | 175 | 360 | 115 | 270 | 275 | 1600 | 4000
| nominal charge capability (A) | 50.4 | 29.4 | 33.6 | 19.6 | 50 | 110 | 400 | 1000
| fast charge capability (A) | 100.8 | 58.8 | 67.2 | 39.2 | 75 | 165 | 400 | 1000
Batterypack specifications
|  | extreme | endurance | extreme | endurance
Item | unit | 21700-12P | 21700-12P | 21700-8P | 21700-8P | LiFePo4 50Ah | LiFePo4 110Ah | LiFePo4 400Ah | LiFePo4 1000Ah
amount of modules in series | #S | 32 | 32 | 32 | 32 | 36 | 36 | 36 | 36
amount of modules parallel | #P | 10 | 8 | 14 | 12 | 10 | 5 | 2 | 1
Total amount of modules | # | 320 | 256 | 448 | 384 | 360 | 180 | 72 | 36
volume | L | 172.8 | 138.24 | 170.24 | 145.92 | 277.2 | 259.2 | 637.92 | 806.4 | Modules/cells only
weight | Kg | 316.16 | 249.856 | 325.696 | 276.096 | 493.2 | 502.2 | 972 | 1476 | Modules/cells only
minimum voltage | V | 80 | 80 | 80 | 80 | 90 | 90 | 90 | 90
nominal voltage | V | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2
maximum voltage | V | 134.4 | 134.4 | 134.4 | 134.4 | 129.6 | 129.6 | 129.6 | 129.6
capacity | Ah | 504 | 470.4 | 470.4 | 470.4 | 500 | 550 | 800 | 1000
Energy | kWh | 58.0608 | 54.1901 | 54.1901 | 54.1901 | 57.6 | 63.36 | 92.16 | 115.2 | If larger then 1,25x desired capacity (module/cel is too large)
Continuous discharge current* | A | 3000 | 920 | 2800 | 900 | 1000 | 550 | 2400 | 3000
Maximum discharge current 50%duty cycle* | A | 4200 | 1400 | 3920 | 1380 | 2700 | 1375 | 3200 | 4000
Peak discharge current* | A | 5400 | 1400 | 5040 | 1380 | 2700 | 1375 | 3200 | 4000
Continuous discharge power* | kW | 345.6 | 105.984 | 322.56 | 103.68 | 115.2 | 63.36 | 276.48 | 345.6
Maximum discharge power* | kW | 483.84 | 161.28 | 451.584 | 158.976 | 311.04 | 158.4 | 368.64 | 460.8 | If discharge power smaller then required)
Peak discharge power* | kW | 622.08 | 161.28 | 580.608 | 158.976 | 311.04 | 158.4 | 368.64 | 460.8
nominal charge capability* | A | 504 | 235.2 | 470.4 | 235.2 | 500 | 550 | 800 | 1000
nominal charge capability* | kW | 58.0608 | 27.095 | 54.1901 | 27.095 | 57.6 | 63.36 | 92.16 | 115.2
fast charge capability* | A | 1008 | 470.4 | 940.8 | 470.4 | 750 | 825 | 800 | 1000
fast charge capability* | kW | 116.1216 | 54.1901 | 108.3802 | 54.1901 | 86.4 | 95.04 | 92.16 | 115.2
* assuming the layout of the battery pack supports this theoretical output, such as busbar sizing
If you're not sure about the power needed for your application our engineers can give you a helping hand. Send your question or request here and we'll help to get you started.
www.powerbattery.nl